Int. No. 11

By Council Members Ignizio, Matteo, Williams, Barron, Arroyo, Chin, Koo, Palma, Vallone, Lancman, Cohen, Rose, Levine, Dickens, Johnson, Vacca, Garodnick, Weprin, Ferreras, Rosenthal, Espinal, Cabrera, Constantinides, Cornegy, Crowley, Deutsch, Dromm, Gentile, Gibson, Greenfield, King, Koslowitz, Lander, Levin, Maisel, Mealy, Menchaca, Mendez, Miller, Richards, Torres, Wills, Reynoso, Cumbo, Kallos, Rodriguez, Treyger, Van Bramer, Eugene and Ulrich

..Title

A Local Law to amend the administrative code and the Building Code of the city of New York, in relation to requiring carbon monoxide detectors in certain assembly spaces.

..Body

Be it enacted by the Council as follows:

Section 1. Article 312 of Chapter 3 of title 28 of the administrative code of the city of New York, as added by local law number 75 for the year 2011, is amended by adding a new section 28-312.6 to read as follows:

§28-312.6. Carbon monoxide alarms or detectors required for certain existing assembly spaces. In all existing spaces classified as occupancy group A-1, A-2 or A-3, carbon monoxide alarms or detectors shall be installed in accordance with Section BC 908.7.2 by May 1, 2014.

§2. Section BC 908.7.2 of the New York city building code is amended to read as follows:

§908.7.2 Group A-1, A-2, A-3, E, I-2 and I-4 occupancies. Listed carbon monoxide detectors with built-in sounder bases shall transmit a signal to a central supervising station and shall be permitted to initiate an audible and visual supervisory alarm at a constantly attended location.

- Carbon monoxide detectors with built-in sounder bases shall be installed within any room containing carbon monoxide-producing equipment.

Exception: Kitchens or laboratories.

- Carbon monoxide detectors with built-in sounder bases shall be installed in corridors on the story where carbon monoxide-producing equipment unit is located, as well as one story above and one story below.

- Carbon monoxide detectors with built-in sounder bases shall be installed in all corridors on the story where enclosed parking is located, as well as one story above and one story below.

§3. This local law shall take effect on October 1, 2014.

Int 1008/2013

LS 56/2014

4/7/2014 4:12 PM