Russell Unger

Counsel to the Committee

Michele Kalafer

Legislative Policy Analyst

## THE COUNCIL

###### Report of the Governmental Affairs Division

Marcel Van Ooyen, Deputy Chief of Staff & Director

COMMITTEE ON FIRE & CRIMINAL JUSTICE SERVICES

Hon. Yvette D. Clarke, Chair

## April 26, 2004

INT. NO. 247:	By Council Members Clarke, Koppell, Seabrook and Stewart (by request of the Mayor)

TITLE:	To amend the administrative code of the city of New York, in relation to mechanical refrigeration and to repeal subchapter 18 of chapter 4 of title 27 relating to mechanical refrigeration.

I. Introduction

On April 26, 2004 the Committee on Fire and Criminal Justice Services, chaired by Council Member Yvette Clarke, will hold a hearing on Int. 247, a local law to amend the administrative code of the city of New York, in relation to mechanical refrigeration and to repeal subchapter 18 of chapter 4 of title 27 relating to mechanical refrigeration.  Those expected to testify include representatives of the Fire Department and fire unions.

II. Background

The requirements in the Fire Prevention Code governing mechanical refrigeration systems installed on or after December 6, 1968 are outdated or superceded by Building Code Reference Standard RS 13-6, which incorporates the 1978 American Society of Heating and Refrigeration and Air Conditioning Engineers (ASHRAE) 15 standard.  The 2001 edition of the ASHRAE 15 standard reclassifies existing refrigerants and classifies new refrigerants with greater emphasis on toxicity and flammability.

III. Int. 247

Int. 247 would repeal and re-enact Subchapter 18 of the Fire Prevention Code, which regulates the installation and testing of mechanical refrigeration systems.  As indicated in the Memorandum in Support of Int. 247, “the new Article 1 would retain and clarify the operating requirements for refrigerating systems, including the requirement that a Fire Department permit be obtained for such systems and that they be operated by a refrigerating system operating engineer holding a Fire department certificate of qualification.”  The Article “would use the refrigerant classifications to be set forth in new amendments to Building Code Reference Standard RS 13-6, to be adopted in conjunction with this local law, and would include a new §27-4191 and a new table, which together would clarify the requirements for supervision of refrigerating systems when they are in operation.”

The standards for systems installed before December 6, 1968 are contained in Subchapter 18, and Article 2 clarifies they would remain unchanged after repeal and re-enactment of the subchapter.  Article 2 also specifies that the standards for systems installed on or after December 6, 1968 are governed by Reference Standard RS 13-6.

The bill would amend related sections of the Fire Prevention Code. As explained in the Memorandum in Support, “Section 27-4002 would be amended to make the term ‘department’ a defined term meaning the Fire Department, and to include a definition for ‘refrigerating system,’ which is presently set forth in §27-4112 (qq) in a provision of Subchapter 18 that is to be repealed.  Section 27-4026 would be amended to substitute the term ‘refrigerating system operating engineer’ for the existing term ‘qualified refrigeration operator.’”

The bill would also amend related sections of the Building Code.  The Memorandum in Support indicates that “Section 27-106 would be amended to give the Fire Department the ability to enforce Building Code provisions governing the maintenance and operation of refrigerating systems and oil-burning equipment, and those requiring the posting and/or on-site availability of certificates of occupancy and equipment use permits (Buildings Department approvals needed to obtain Fire Department operating permits).  Section 27-184 would be amended to refer to the new refrigerant classification standards to be set forth in new amendments to Building Code Reference Standard RS 13-6.”

Int. No. 247

..Title A Local Law to amend the administrative code of the city of New York, in relation to mechanical refrigeration and to repeal subchapter 18 of chapter 4 of title 27 relating to mechanical refrigeration. ..Body

By Council Members Clarke, Koppell, Seabrook and Stewart (by request of the Mayor) Be it enacted by the Council as follows:

Section 1.  Section 27-106 of the administrative code of the city of New York is amended to read as follows:

§ 27-106 Enforcement.   This code shall be enforced by the commissioner of buildings, pursuant to the provisions of section six hundred forty three of the New York city charter, as amended, except that the fire commissioner shall also enforce the provisions of this code relating to the approved number of persons in places of assembly (overcrowding), obstruction of aisles, corridors, and exits, the posting and availability for inspection of equipment use permits, and the availability for inspection of certificates of occupancy or other authorization of lawful occupancy, and to the maintenance of installations involving fire alarm equipment and devices, exit and directional signs, emergency lighting, [and] fire-preventative and fire extinguishing equipment and devices, [and] refrigerating systems, and storage tanks and auxiliary storage tanks for oil burning equipment, except that the commissioner of [ports and terminals] small business services, shall enforce all the provisions of this code with respect to buildings under the jurisdiction of the department of [ports and terminals] small business services.  Where the installation of exit and directional signs, emergency lighting and sprinkler and fire alarm protection is required by the fire prevention code, the fire commissioner shall require such installations to be in accordance with the provisions of this code.

§ 2.  Section 27-114 of the administrative code of the city of New York is amended by adding a new subdivision (h) to read as follows:

(h)   The installation, alteration or replacement of refrigerating systems as provided in reference standard RS 13-6.

§  3.  Paragraph 1 of  subdivision (d) of  section 27-184 of  the administrative code of the city of New York is amended to read as follows:

1.  Has a capacity of twenty-five tons or less and uses a Group [I] A1 refrigerant.

§  4.   Subdivision (c) of  section 27-781 of the administrative code of the city of New York is  amended to read as follows:

(c) Exception.  No equipment use permit or temporary equipment use permit shall be required for any [refrigeration] refrigerating system exempted under the provisions of section 27-189 of article eighteen of subchapter one of this chapter; for any system using a group [two] A2, B1 or B2  refrigerant and having a prime mover of one [h. p.] horsepower or less; or for any system using water or air as a refrigerant.

§  5.  Paragraph (3) of subdivision (b) of section 27-946 of the administrative code of the city of New York is amended to read as follows:

(3)  No person shall place or install any equipment containing a refrigerant classified in groups [I, II, and III] A1, A2, A3, B1, B2 or B3 in subchapter thirteen of this chapter, or place or install gas piping or gas consuming devices or any other equipment within any space housing a fire pump that would create a hazardous condition.

§ 6.  Section 27-4002 of the administrative code of the city of New York is amended adding a new subdivision 10c to read as follows:

10c.  Department, the fire department of the city of New York.

§  7.  Section 27-4002 of the administrative code of the city of New York is amended by adding a new subdivision 47 to read as follows:

47.  Refrigerating system, a combination of interconnected refrigerant-containing parts forming a closed circuit in which refrigerant is circulated for the purpose of extracting, then discharging heat.

§  8.  Paragraph 2 of subdivision (a) of section 27-4026 of the administrative code of the city of New York,  as amended by local law 32 for the year 1987,  is amended to read as follows:

2.  Certificate of qualification [to operate] for refrigerating [systems;] system operating engineer:

Original [for a term of three years] ………………….$25.00

Renewals  [for terms of three years]………………….$5.00

§  9.  Paragraph 1 of subdivision p of § 27-4027 of the administrative code of the city of New York, as amended by local law 43 for the year 1988, is amended to read as follows:

1.	to maintain [and/] or operate [refrigeration units]  a refrigerating system

[equal to or above 5 H.P., and/or roof mounted/suspended, and/or ceiling            mounted/suspended,  or units using group II or group III refrigerants] (per [unit] compressor)…………………………………  105.00

§  10.  Subchapter 18 of chapter 4 of title 27 of the administrative code of the city of New York is REPEALED and a new subchapter 18 is reenacted  to read as follows:

SUBCHAPTER 18

MECHANICAL REFRIGERATION

ARTICLE  1

PERMITS AND  OPERATING REQUIREMENTS

§27-4190 Permits.   a.  For purposes of this subchapter, refrigerants shall be classified by safety groups in accordance  with reference standard RS 13-6 of the building code.   Except as otherwise provided in this subchapter, it shall be unlawful to maintain or operate without a permit any  refrigerating  system that uses a group A1,  A2,  A3,  B1,  B2 or B3 refrigerant or that is mounted on or suspended from a roof or ceiling, except a refrigerating system of  less than five  horsepower that uses a group A1 refrigerant and that is not mounted on or suspended from a roof or ceiling.  Such permit shall be posted adjacent to the system or kept on the premises in a location where it can be produced upon request of any representative of the department.

b.  Permits shall not be required for  refrigerating systems installed in the residence portion of any building;  installed in vehicles, vessels or railroad cars;  or employing water or air as a refrigerant.

c.   The system capacity of a refrigerating system with multiple compressors shall be the aggregate of all the individual compressors.

d.    If the department finds that the system creates a hazard to life or property or for other good cause, it may order the system to be shut down until the corrections required by the department are made.

§  27-4191 Refrigerating system operating engineer.  a.  It shall be unlawful to operate any refrigerating system for which a permit is required under this subchapter and which is a system described in Table 1 of this subchapter, unless such operation is under either the personal supervision or general supervision, as specified in Table 1, of a person who has obtained a certificate of qualification for refrigerating system operating engineer.  For purposes of this subchapter, personal supervision shall mean that such person is present on the premises or other proximate location acceptable to the commissioner at all times while the system is in operation and that the operation of such system is under his or her personal direction and control, and general supervision shall mean that such person is responsible at all times for the safe operation of such system when such system is in operation but need not be personally present on the premises at all times while the system is in operation.

b.   A certificate of qualification for refrigerating system operating engineer shall be issued by the commissioner to an applicant who has been certified as qualified to operate a refrigerating system and otherwise meets the requirements established for such certificate of qualification, including appropriate experience and/or training in refrigerating systems or related technology.  For purposes of issuing such certificate of qualification, the commissioner may approve training courses in refrigeration and related technology.

### TABLE 1
REFRIGERATING SYSTEM OPERATING ENGINEER

| INSTALLATION DATE | REFRIGERANT GROUP OR NAME (see note 1) | OCCUPANCY TYPE (see note 2) | APPLICATION | POUNDS OF REFRIGERANT IN SYSTEM | SYSTEM HORSE-POWER | SYSTEM DESIGN | SUPERVISION REQUIREMENT |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Prior to June 1, 1957 | A1 | Industrial | Human comfort | More than 50 | NA | Not fully automatic | Personal |
|  | A1 | Industrial | Human comfort | More than 200 | NA | Fully automatic | Personal |
|  | A1 | Industrial | Human comfort | More than 50 up to 200 | NA | Fully automatic | General |
|  | A1 | All except Industrial | All | More than 50 | NA | Not fully automatic | Personal |
|  | A1 | All except Industrial | All | More than 200 | NA | Fully automatic | Personal |
|  | A1 | All except Industrial | All | More than 50 up to 200 | NA | Fully automatic | General |
| On or after June 1, 1957 | A1 | Industrial | Human comfort | NA | More than 50 (or kilowatt equivalency) (see note 3) | NA | Personal |
|  | A1 | All except Industrial | All | NA | More than 50 (or kilowatt equivalency) (see note 3) | NA | Personal |
| Regardless of when installed | A2, A3, B1, B2, B3 and carbon dioxide | All | All | More than 50 | NA | Not fully automatic | Personal |
|  | A2, A3, B1, B2, B3 and carbon dioxide | All | All | More than 200 | NA | Fully automatic | Personal |
|  | A1 | Industrial | All except human comfort | More than 50 | NA | Not fully automatic | Personal |
|  | A1 | Industrial | All except human comfort | More than 200 | NA | Fully automatic | Personal |
|  | A1 and carbon dioxide | Industrial | All except human comfort | More than 50 up to 200 | NA | Fully automatic | General |
|  | A1 | All | Human comfort | NA | Aggregate exceeds 100 (see note 4) | NA | Personal |

Notes:

1.	For purposes of refrigerating system operating engineer requirements, Refrigerant R-123 shall be treated as a group A1 refrigerant, and carbon dioxide shall not be treated as a group A1 refrigerant.

2.	For installations after December 6, 1968, industrial occupancy refers to occupancy groups A, B-1, B-2, D-1 and D-2 as defined in chapter 1 of this title.  For installations prior to such date, industrial occupancy refers to that portion of a building used for manufacturing, processing, or storage of materials or products, including, among others, chemical, food, candy, and ice cream factories, ice making plants, meat packing plants, refineries, perishable food warehouses, and similar occupancies.

3.	This provision shall not apply to installations approved prior to the effective date of the local law that added §27-4191 of this subchapter.  However, an operator shall be required for all systems which contain any single prime mover or compressor in excess of 50 horsepower.

4.	This aggregate provision applies only to systems within a single building which are under the sole direct control of a single occupant, lessee or owner.  Systems with a rating of 15 horsepower or less or the kilowatt equivalency thereof are excluded from the aggregate.

ARTICLE 2

INSTALLATION, CLASSIFICATION, TESTING AND REFRIGERANT REQUIREMENTS

§  27-4192 Applicable Requirements.  a.  All refrigerating systems installed on or after the sixth day of December, nineteen hundred sixty-eight shall be subject to the requirements of the building code and reference standards and rules promulgated thereunder.

b.  All refrigerating systems installed prior to the sixth day of December, nineteen hundred and sixty-eight shall be subject to the requirements of this subchapter in effect prior to the effective date of the local law that added this section, except where such installations are altered or replaced, in which event such refrigerating systems shall be subject to the requirements of the building code and reference standards and rules promulgated thereunder.

§  18.  This local law shall take effect immediately.