Staff:	Edward Atkin, Counsel to the Committee

Cullen Howe, Legislative Counsel

Guillermo Patino, Legislative Policy Analyst

Jose Conde, Legislative Policy Analyst

Sarah Gastelum, Legislative Financial Analyst

THE COUNCIL

REPORT OF THE INFRASTRUCTURE DIVISION

ROBERT NEWMAN, LEGISLATIVE DIRECTOR

COMMITTEE ON HOUSING AND BUILDINGS

Jumaane D. Williams, Chair

April 29, 2014

PROPOSED INT. NO. 16-A:	By Council Members Levin, Chin, Koo, Palma, Williams, Johnson, Mendez, Richards, Lancman, Rosenthal, Arroyo and Levine

TITLE:	A Local Law to amend the administrative code of the city of New York, in relation to requiring insulation of existing concealed pipes exposed during alteration or repair.

ADMINISTRATIVE CODE:	Adds a new article 316 to title 28.

PROPOSED INT. NO. 93-A:	By Council Members Matteo, Ignizio, Gentile, Rose Richards, Rosenthal, Arroyo and Ulrich (by request of the Staten Island Borough President)

TITLE:	A Local Law to amend the New York city building code, in relation to requiring the use of mold-resistant gypsum board and cement board in moisture-prone areas.

ADMINISTRATIVE CODE:	Amends section 28-101.4.3.

BUILDING CODE:	Amends sections 2501.1.1, 2502.1 and chapter 35. Adds section 2506.3.

PROPOSED INT. NO. 203-A:	By Council Members Koo and Arroyo

TITLE:	A Local Law to amend the administrative code of the city of New York, the New York city building code and the New York city fire code, in relation to hold-open devices and automatic closing of exit doors serving vertical exit enclosures.

ADMINISTRATIVE CODE:	Amends section 28-101.4.4.

BUILDING CODE:	Amends sections 708.7, 715.4.8.3, 911.1.5, 1022.1, and 1022.8. Adds new sections 907.3.5 and 1022.8.5.

FIRE CODE:	Amends sections 703.2.2. Adds new section 907.20.7.

PROPOSED INT. NO. 263-A:	By Council Member Levin, Chin, Rose and Arroyo

TITLE:	A Local Law to amend the New York city building code, in relation to construction site lighting.

BUILDING CODE:	Adds section 3303.2.3.1.

Introduction

On April 29, 2014, the Committee on Housing and Buildings, chaired by Council Member Jumaane D. Williams, will vote on Proposed Int. No. 16-A, Proposed Int. No. 93-A, Proposed Int. No. 203-A, and Proposed Int. No. 263-A.

The Committee previously considered these bills at a hearing held on April 2, 2014 and received testimony from the Department of Buildings, the Office of Long Term Planning and Sustainability, environmental advocates, engineers, architects, builders, building managers, members of the real estate industry,	 and other interested members of the public.

Background

By enacting Local Law 22 of 2008, New York City committed to reducing its greenhouse gas emissions by 30% by 2017 for government operations and by 30% citywide by 2030. Buildings are responsible for about 75% of our greenhouse gas emissions, making improved building efficiency a crucial component of reaching these environmental goals.

Recognizing the important role of building performance, in July 2008 the New York City Green Codes Task Force was convened. The Task Force was composed of industry experts, union representatives, tenant advocates, environmentalists, academics, developers, buildings owners, and representatives of City agencies as well as the Mayor’s office and the City Council. This group was divided into nine technical committees, a steering committee, and an industry advisory committee. After two years of work examining each of New York City’s construction codes, the task force presented 111 recommendations for “greening the codes.” The recommended improvements are intended to raise the bar for environmental performance in buildings throughout the City. Moreover, by standardizing green building practices it is believed that economies of scale will be achieved, bringing down the cost of “building green.” Since the report was released, 47 of the recommendations have been incorporated into the City’s laws and practices.

Proposed Int. No. 16-A

Proposed Int. No. 16-A would require insulation of existing concealed pipes exposed during alteration or repair. Uninsulated pipes are a common problem in New York City buildings, which, by allowing heat to escape through walls, can lead to overheating and wasted energy.  The bill would reduce energy use and improve occupant comfort by ensuring that pipes exposed during alterations or repairs are properly insulated.

Bill section one adds a new article 316 to title 28 of the administrative code to require that concealed piping exposed during alterations or repairs be insulated as if it was newly installed piping.  This requirement would apply to the entire length of pipe that is exposed and reasonably reachable.  Exceptions are made for piping that already has insulation that is in good condition, where the length of pipe exposed and accessible is less than three feet, and where there is not sufficient space to insulate pipes to the extent required by the New York City Energy Conservation Code due to conflicts with existing construction.

Bill section two sets an effective date of October 1, 2014 for the bill.

Changes to Proposed Int. No. 16-A

The changes made to Proposed Int. No. 16-A include the following:

- An exception was added stating that where there is not sufficient space to insulate pipes to the extent required by the New York City Energy Conservation Code due to conflicts with existing construction, pipes are to be insulated to the extent that space allows.

- Technical changes were made throughout the bill.

Proposed Int. No. 93-A

Proposed Int. No. 93-A would require the use of mold-resistant gypsum board and cement board in moisture-prone locations.  Molds are known allergens, irritants, and producers of toxic substances (mycotoxins) which can trigger asthma attacks and other chronic conditions.  This bill requires the use of cement board in shower areas and bath surrounds and requires the use of gypsum board or cement board with a certain mold resistance rating in specified areas where there is continuous high humidity or direct exposure to water.

Bill section one amends section 28-101.4.3 of the administrative code to add an exception stating that alterations comply with sections 2506 and 2509 of the building code relating to areas subject to moisture or water damage.

Bill section two amends section 2501.1.1 of the building code, by stating that the provisions of the chapter also apply to cement board.

Bill section three adds a definition for cement board to section 2502.1 of the building code.

Bill section four adds a new section 2506.3 to the building code that requires that gypsum board or cement board used in the assembly of certain areas have a mold resistance rating of 10 in accordance with an industry standard.  These areas include the interior faces of exterior walls of basements, cellars and other below grade rooms; walls and ceilings of spaces containing condensers, water tanks, water pumps, and pressure reduction valves; walls and ceilings of laundry rooms; portions of walls within two feet of kitchen sinks to a height of four feet above the floor; portions of walls within two feet of kitchen stoves to a height of four feet above the floor; walls of bathrooms that are not solely water closet compartments; walls and ceilings in service sink closets; and portions of walls within two feet of mop sinks or service sinks to a height of four feet above the floor.

Bill section five adds new reference standard ASTM D3273-12 to the list of reference standards in chapter 35 of the building code.

Bill section six sets an effective date of October 1, 2014 for the bill.

Changes to Proposed Int. 93-A

The changes made to Proposed Int. No. 93-A include the following:

- The definition of cement board was expanded and clarified.

- Section four of the bill was changed to state that gypsum board or cement board, used in certain areas, are to have a certain mold resistance rating pursuant to an industry standard.

- Section four of the bill was also revised to state that the following areas were required to have such gypsum board or cement board:  interior faces of exterior walls of basements, cellars and other below grade rooms; walls and ceilings of spaces containing condensers, water tanks, water pumps, and pressure reduction valves; walls and ceilings of laundry rooms; portions of walls within two feet of kitchen sinks to a height of four feet above the floor; portions of walls within two feet of kitchen stoves to a height of four feet above the floor; walls of bathrooms that are not solely water closet compartments; walls and ceilings in service sink closets; and portions of walls within two feet of mop sinks or service sinks to a height of four feet above the floor.

- Section five of the bill deleted two of the ASTM referenced standards to be included in Chapter 35 of the New York City building code.

- The effective date of the law was changed from January 1, 2015 to October 1, 2014.

- Technical changes were made throughout the bill.

Proposed Int. No. 203-A

This bill allows the use of hold-open devices and automatic closing of exit doors in certain stairways to encourage the use of stairs by occupants. The hold-open devices would automatically release if smoke was detected.

Bill section one amends section 28-101.4.4 of the administrative code by adding an exception for the use of automatic closing doors by smoke detection for prior code buildings.

Bill section two amends section 708.7 of the building code by adding exceptions that allow for the automatic closing of doors serving vertical exit enclosures by smoke detection in certain buildings. Doors serving vertical exit enclosures that are permitted to be automatic closing by smoke detection are subject to certain conditions.

Bill section three amends section 715.4.8.3 of the building code to allow doors serving vertical exit enclosures to be automatic closing by smoke detection.

Bill section four adds a new section 907.3.5 to the building code requiring that all hold-open devices used in automatic closing doors be electrically supervised to monitor the integrity of the wiring connections.

Bill section five amends section 911.1.5 of the building code to require manual controls for the release of doors that are automatic closing by the actuation of smoke detectors or activation of the fire alarm.

Bill section six amends section1022.1 of the building code to allow vertical enclosures with doors that are automatic closing to be used for travel between floors.

Bill section seven adds a new section 1022.8.5 to the building code requiring that, where doors serving vertical exit enclosures are locked on the stair side, signage shall be posted.

Bill section eight amends section 703.2.2 of the fire code to require that automatic door closers for self-closing fire doors be inspected, tested, and otherwise properly maintained.

Bill section nine amends section 907.20 of the fire code by adding a new subdivision 907.20.7 setting certain requirements for the inspection and testing of fire alarm system connections for hold-open devices installed on fire doors.

Bill section nine sets an effective date of October 1, 2014 for the bill.

Changes to Proposed Int. 203-A

The changes made to Proposed Int. No. 203-A include the following:

- The effective date of the law was changed from immediately to October 1, 2014.

- Technical changes were made throughout the bill.

Proposed Int. No. 263-A, in relation to construction site lighting

New York City construction sites are commonly illuminated with inefficient incandescent light bulbs. This bill would set minimum illumination efficacy standards for temporary construction site lighting.

Bill section one amends section 3303.2.3.1 of the building code by requiring that lighting for construction sites shall use high-efficacy lamps.

Bill section two sets an effective date of October 1, 2014.

Changes to Proposed Int. 263-A

The changes made to Proposed Int. No. 263-A include the following:

- Portions of section three of the bill, which stated that construction lighting had to be controlled by one or more master switches and that general construction lighting was to be separately circuited from safety construction lighting, were removed.

- The effective date of the law was changed from January 1, 2015 to October 1, 2014.

- Technical changes were made throughout the bill.

Update

On Tuesday, April 29, 2014, the Committee adopted this legislation.  Accordingly, the Committee recommends its adoption.

Proposed Int. No. 16-A

By Council Members Levin, Chin, Koo, Palma, Williams, Johnson, Mendez, Richards, Lancman and Rosenthal

A LOCAL LAW

To amend the administrative code of the city of New York, in relation to requiring insulation of existing concealed pipes exposed during alteration or repair.

Be it enacted by the Council as follows:

Section 1. Chapter 3 of title 28 of the administrative code of the city of New York, as amended by local law number 141 for the year 2013, is amended by adding a new article 316 to read as follows:

ARTICLE 316

INSULATION OF CONCEALED PIPES EXPOSED DURING ALTERATION OR REPAIR

§ 28-316.1 Required insulation of certain concealed piping exposed during alteration or repair. Where concealed existing piping is exposed in the course of the alteration or repair of a building, the owner of the building shall provide for the insulation of the exposed piping. The exposed piping shall be insulated to the extent required by the New York city energy conservation code for newly installed pipe of the same specifications and serving the same function as the exposed pipe. The entire exposed length of the piping shall be insulated as well as any further length of concealed pipe that can be directly accessed through openings made in the course of such alteration or repair.

Exceptions:

1. 	Exposed pipe with one-inch (25-mm) thick continuous coverage of existing insulation in good condition.

2. 	Where the length of concealed pipe which may be directly accessed through openings made in the course of such alteration or repair is less than three feet (914 mm).

3. 	Where there is not sufficient space to insulate pipes to the extent required by the New York city energy conservation code due to conflicts with existing construction, pipes shall be insulated to the extent that space allows.

§2. This local law shall take effect October 1, 2014, except that this local law shall not apply to construction work related to applications for construction document approval filed prior to such effective date, and except that the commissioner of buildings may take such measures as are necessary for its implementation, including the promulgation of rules, prior to such effective date.

LS # 98

4/21/2014 10:20PM

Proposed Int. No. 93-A

By Council Members Matteo, Ignizio, Gentile, Rose, Richards and Rosenthal (by request of the Staten Island Borough President)

A LOCAL LAW

- To amend the administrative code of the city of New York and the New York city building code, in relation to requiring the use of mold-resistant gypsum board and cement board in moisture-prone locations.

Be it enacted by the Council as follows:

Section 1.  Section 28-101.4.3 of the administrative code of the city of New York, as amended by local law numbers 130 and 141 for the year 2013, is amended to add a new exception 19 to read as follows:

19. Mold protection. Alterations shall comply with sections 2506 and 2509 of the New York city building code relating to areas subject to moisture or water damage.

§ 2. Section 2501.1.1 of chapter 25 of the New York city building code, as added by local law number 33 for the year 2007, is amended to read as follows:

2501.1.1 General.  Provisions of this chapter shall govern the materials, design, construction and quality of gypsum board, lath, gypsum plaster, [and] cement plaster and cement board.

§ 3. Section 2502.1 of chapter 25 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding a definition for “CEMENT BOARD,” in appropriate alphabetical order, to read as follows:

CEMENT BOARD. A fiber reinforced cementitious panel most commonly used under flooring or as a tile backing board. Cement board shall include discrete nonasbestos fiber-cement interior substrate sheets or nonasbestos fiber-mat reinforced cement substrate sheets.

§ 4. Chapter 25 of the New York City building code, as amended by local law number 141 for the year 2013, is amended by adding a new section 2506.3 to read as follows:

2506.3 Mold resistance. Gypsum board or cement board, used in an assembly for the following areas, shall have a mold resistance rating of 10 in accordance with ASTM D3273:

1.	Interior faces of exterior walls of basements, cellars, and other below grade rooms;

2.	Walls and ceilings of spaces containing condensers, water tanks, water pumps, and pressure reduction valves;

3.	Walls and ceilings of laundry rooms;

4.	Portions of walls within 2 feet (610 mm)  of kitchen sinks to a height of 4 feet (1219 mm) above the floor;

5.	Portions of walls within 2 feet (610 mm) of kitchen stoves to a height of 4 feet (1219 mm) above the floor;

6.	Walls of bathrooms that are not solely water closet compartments, other than walls specifically required to be cement board;

7.	Walls and ceilings in service sink closets; and

8.	Portions of walls within 2 feet (610 mm) of mop sinks or service sinks to a height of 4 feet (1219 mm) above the floor.

§ 5.  The list of ASTM referenced standards in chapter 35 of the New York city building code is amended by adding a new reference standard “ASTM D3273 – 12” to read as follows:

| ASTM | ASTM International 100 Barr Harbor Drive West Conshohocken, PA 19428-2959 |  |
| --- | --- | --- |
| Standard Reference Number | Title Referenced in code section number |  |
| D 3273 – 12 | - Standard Test Method for Resistance to Growth of Mold - on the Surface of Interior Coatings in an Environmental Chamber . . . . . . . . . . . . . . . . . . . . . . . . | 2506.3 |

§ 6.  This local law shall take effect on October 1, 2014, except that this local law shall not apply to construction work related to applications for construction document approval filed prior to such effective date, and except that the commissioner of buildings shall take such measures as are necessary for its implementation, including the promulgation of rules, prior to such effective date.

Int. 1186-2013

LS # 622

4/21/2014 10:34PM

Proposed Int. No. 203-A

By Council Member Koo

A LOCAL LAW

To amend the administrative code of the city of New York, the New York city building code and the New York city fire code, in relation to hold-open devices and automatic closing of exit doors serving vertical exit enclosures.

Be it enacted by the Council as follows:

Section 1. Section 28-101.4.4 of the administrative code of the city of New York, as amended by local law number 141 for the year 2013, is amended by adding a new exception to read as follows:

Exception: The use of automatic-closing by smoke detection for doors serving vertical exit enclosures in accordance with section 708.7 of the New York city building code in a prior code building shall not be deemed to result in a reduction of the fire safety or structural safety of such a building.

§2. Section 708.7 of the New York city building code, as amended by local law number 141 for the year 2013, is amended to read as follows:

708.7 Openings.  Openings in a shaft enclosure shall be protected in accordance with Section 715 as required for fire barriers. Doors shall be self-closing or automatic-closing by smoke detection in accordance with Section 715.4.8.3. Automatic-closing by smoke detection is not permitted for [required vertical exit] doors serving vertical exit enclosures.

Exception:  For no more than one vertical exit enclosure in a building, doors serving such enclosure may be automatic-closing by smoke detection provided that the following conditions are satisfied:

1. The building contains no Group H space and:

1.1	Is not a high-rise building pursuant to Section 403.1 of this code or, for the purposes of prior code buildings, Section 27-232 of the Administrative Code, and is equipped with a fire alarm system; or

1.2	Is equipped with fire alarm systems and automatic sprinkler systems throughout; or

1.3	Is a high-rise office building, as such term is defined in Section 27-232 of the Administrative Code, that is 100 feet (30 480 mm) or more in height, equipped with a fire alarm system and subdivided into compartments pursuant to subdivision c of Section 27-339 of the Administrative Code.

2.	Such doors serve no more than three levels within such vertical exit enclosure, which must be consecutive levels.

3.	All levels served by such doors are served by at least one other exit.

4.	Such doors are connected to a fire alarm system and installed in accordance with Section 715.4.8.3 and NFPA 80.

5.	The hold-open devices of such doors:

5.1	Are capable of manual release at the fire command center or, if a fire command center is not required, at a fire alarm control panel that is near the main building entrance; and

5.2	Are capable of manual release by pulling the doors to the closed position.

§3.  Section 715.4.8.3 of the New York city building code, as amended by local law number 141 for the year 2013, is amended by adding a new item 12 to read as follows:

12.  Doors serving vertical exit enclosures in accordance with the exception to Section 708.7.

§4.   Section 907.3 of the New York city building code, as added by local law 141 for the year 2013, is amended by adding a new section 907.3.5 to read as follows:

907.3.5 Monitoring of hold-open devices and closers. All hold-open devices used in automatic-closing doors pursuant to the exception to Section 708.7 shall be electrically supervised to monitor the integrity of the wiring connections among the fire alarm system, the smoke detection system, and the hold-open devices.

§5.  Section 911.1.5 of the New York city building code, as added by local law number 141 for the year 2013, is amended by adding a new item 8 to read as follows:

8. Manual controls for the release of doors that are automatic-closing by the actuation of smoke detectors or activation of the fire alarm in accordance with the exception to Section 708.7.

§6.  Section 1022.1 of the New York city building code, as amended by local law number 141 for the year 2013, is amended by adding a new exception 8 to read as follows:

8.  Vertical exit enclosures with doors that are automatic-closing by smoke detection pursuant to the exception set forth in Section 708.7 may be used for travel between floors and this use shall not be deemed to interfere with function as a means of egress.

§7.  Section 1022.8 of the New York city building code, as amended by local law number 141 for the year 2013, is amended to read as follows:

1022.8 Stairway identification and floor level signs. Signs identifying stairways and floor levels shall comply with Sections 1022.8.1 through [1022.8.4] 1022.8.5.

§8.  Section 1022.8 of the New York city building code, as amended by local law number 141 for the year 2013, is amended by adding a new section 1022.8.5 to read as follows:

1022.8.5 Directions to openable doors. Where doors serving vertical exit enclosures are locked on the stair side, signage shall be posted in compliance with Sections 1030.4.1, 1030.4.2 and 1030.4.3.

§9.  Section 703.2.2 of the New York city fire code, as added by local law number 148 for the year 2013, is amended to read as follows:

703.2.2  Hold-open devices and automatic door closers.  Hold-open devices for fire doors and automatic door closers for self-closing fire doors, where provided, shall be inspected, tested, and otherwise maintained in accordance with FC 703.2 and 907.20.  During the period that such hold-open device is out of service for repairs, the door it operates shall remain in the closed position.

§10.  Section 907.20 of the New York city fire code, as amended by local law number 148 for the year 2013, is amended by adding a new subdivision 907.20.7 to read as follows:

907.20.7 Hold-open devices.  The fire alarm system connections for hold-open devices installed on fire doors pursuant to the Building Code, including hold-open devices provided for vertical exit enclosure doors pursuant to the exception to Section BC 708.7 of the Building Code, shall be inspected, tested and otherwise maintained in accordance with FC 703.2 and 907.20 and NFPA 72.  Hold-open devices and automatic door closers provided for such vertical exit enclosure doors shall be inspected and tested annually to ensure the proper functioning of:

1.	the manual control on the fire alarm system control panel, or the fire command center where a fire command center is required, that transmits a signal to release the hold-open devices;

2.	the fire alarm system output programming, which automatically transmits a signal to release the hold-open devices upon activation of an automatic alarm initiating device or manual elevator recall;

3.	the circuitry for each hold-open device, which upon receipt of a manual or automatic signal, releases the door; and

4.	each automatic door closer, which, upon release of the door by the hold-open device, mechanically moves the door to its fully closed position.

§ 11.  This local law shall take effect on October 1, 2014, except that this local law shall not apply to construction work related to applications for construction document approval filed prior to such effective date, and except that the commissioner of buildings shall take such measures as are necessary for its implementation, including the promulgation of rules, prior to such effective date.

Int. 1113-2013

LS # 1055

4/21/2014 10:43PM

Proposed Int. No. 263-A

By Council Members Levin, Chin and Rose

A LOCAL LAW

To amend the New York city building code, in relation to construction site lighting.

Be it enacted by the Council as follows:

Section 1. Section 3303.2.3 of the New York city building code is amended by adding a new section 3303.2.3.1 to read as follows:

3303.2.3.1 Temporary lighting for construction sites. Temporary lighting for construction sites shall use high-efficacy lamps with the following minimum efficacies:

1.	60 lumens per watt for lamps over 40 watts;

2.	50 lumens per watt for lamps over 15 watts but less than or equal to 40 watts; and

3.	40 lumens per watt for lamps 15 watts or less.

§2. This local law shall take effect October 1, 2014, except that the commissioner of buildings shall take such measures as are necessary for its implementation.

Int. 1182-2013

LS # 262

4/21/2014 10:38PM

Mayor’s Office of Long-Term Planning and Sustainability, Inventory of New York City Greenhouse Gas Emissions (Sept. 2009).

Urban Green Council, NYC Green Codes Task Force Score Card, available at http://www.urbangreencouncil.org/GreenCodes.