Int. No. 1096

By Council Members Oddo, Chin, Comrie, Dickens, Fidler, James, Koo, Lander, Mendez, Recchia, Richards and Rose

..Title

A Local Law to amend the administrative code of the city of New York, the New York city building code, the New York city mechanical code and the New York city fire code, in relation to relocating and protecting building systems in flood-prone areas.

..Body

Be it enacted by the Council as follows:

Section 1. Article 90 of section 27-3025 of the administrative code of the city of New York, as added by local law number 39 for the year 2011, is amended by adding a new section 90.10 to read as follows:

SECTION 90.10 - Add a new section 90.10 to read as follows:

90.10 Areas of Special Flood Hazard and Areas of Moderate Flood Hazard. Structures located in areas of special flood hazard and areas of moderate flood hazard, as defined in Section BC G201.1 of the New York City Building Code, shall also comply with the provisions of Appendix G of the New York City Building Code. Where, in any specific case, the provisions of this code conflict with the provisions of Appendix G of the New York City Building Code, the more restrictive shall govern.

§2. Section BC 202 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding new definitions of “AREA OF MODERATE FLOOD HAZARD,” “MODERATE FLOOD” and “MODERATE FLOOD ELEVATION” in appropriate alphabetical order to read as follows:

AREA OF MODERATE FLOOD HAZARD. See Section G201.2.

MODERATE FLOOD. See Section G201.2.

MODERATE FLOOD ELEVATION. See Section G201.2.

§3. Section BC G201.2 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding new definitions of “AREA OF MODERATE FLOOD HAZARD,” “MODERATE FLOOD” and “MODERATE FLOOD ELEVATION” in appropriate alphabetical order to read as follows:

AREA OF MODERATE FLOOD HAZARD. The land delineated in the flood plain on the Flood Insurance Rate Map (FIRM) as subject to a chance of flooding that is 0.2 percent or greater, but less than one percent, in any given year. Areas of moderate flood hazard are designated on the FIRM as X-Zones (shaded) and are also known as the five hundred year flood plain.

MODERATE FLOOD. The flood having a 0.2 percent chance of being equaled or exceeded in any given year.

MODERATE FLOOD ELEVATION. The elevation of the moderate flood, including wave height, as specified on the Flood Insurance Rate Map (FIRM) or as determined in accordance with Section G103.3.

§4. The definition of “DESIGN FLOOD ELEVATION” as set forth in section BC G201.2, as amended by local law number 8 for the year 2008, is amended to read as follows:

DESIGN FLOOD ELEVATION. The applicable elevation specified in ASCE 24, Tables 2-1, 4-1, 5-1, 6-1, or 7-1, depending on the structural occupancy category designated in ASCE 24, Table 1-1, except that for I-2 occupancies that are hospitals, the design flood elevation shall be the greater of (i) the moderate flood elevation or (ii) the applicable elevation specified in ASCE 24, Tables 2-1, 4-1, 5-1, 6-1, or 7-1.

§5. Item 4 of section BC G304.1.1 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding  new items 4.1, 4.2, 4.3 and 4.4 to read as follows:

4.1 Fire protection systems and equipment. The following fire protection systems and equipment shall be located at or above the design flood elevation specified in ASCE 24, Table 7-1:

4.1.1. Sprinkler control valves that are not outside stem and yoke valves;

4.1.2. Fire standpipe control valves that are not outside stem and yoke valves;

4.1.3. Sprinkler booster pumps and fire pumps except that, in buildings where all occupied floors are less than 300 feet (91.44 m) in height above the lowest level of Fire Department vehicle access and where locating such pumps above the design flood elevation specified in ASCE 24, Table 7-1, is not feasible, sprinkler systems and fire standpipe systems shall be supplied by gravity tanks in accordance with Section 9.1.4(4) of NFPA 13R as modified in Appendix Q;

4.1.4. Dry pipe valve-related electrically operated alarm appurtenances;

4.1.5. Electrically activated water and non-water fire extinguishing systems;

4.1.6. Electrically activated sprinkler systems, pre-action sprinkler systems, deluge sprinkler systems, and combined dry pipe and pre-action sprinkler systems;

4.1.7. Electrically operated waterflow detection devices serving sprinkler systems; and

4.1.8. Air compressors serving sprinkler systems;

4.2. Fire alarm systems and components. At least one zoning indicator panel required in Section BC 907.8.1 of this code shall comply with the following additional requirements:

4.2.1. The zoning indicator panel and associated controls shall be provided at least five feet (1524 mm) above the design flood elevation specified in ASCE 24, Table 7-1, in a location approved by the department and the Fire Department;

4.2.2. Where the zoning indicator panel or associated controls are only operable upon transfer of control from another zoning indicator panel, such transfer shall be by a means that is approved by the Fire Department;

4.2.3. All power supplies for the zoning indicator panel and associated controls, the means of transferring control to the zoning indicator panel and all elements of the fire alarm system shall be located at least five feet (1524 mm) above the design flood elevation specified in ASCE 24, Table 7-1;

4.3 Fuel-oil piping systems. The following requirements shall apply to fuel-oil piping systems, as defined by Section MC 202 of the New York city mechanical code:

4.3.1 Fill piping shall terminate three feet (914 mm) above the greater of (i) the design flood elevation specified in ASCE 24, Table 7-1, or (ii) the moderate flood elevation;

4.3.2 Normal vent piping and emergency vent piping shall terminate three feet (914 mm) above the design flood elevation specified in ASCE 24, Table 7-1;

4.4 Plumbing systems and components. The structure shall comply with the following requirements:

4.4.1 Relief vents and fresh air intakes. Relief vents and fresh air intakes serving building traps in accordance with Section PC 1002.6 of the New York city plumbing code shall be carried above grade and shall terminate in a screened outlet that is located outside of the building and at or above the design flood elevation specified in ASCE 24, Table 7-1;

4.4.2 Reduced pressure zone backflow preventers. Reduced pressure principle backflow preventers complying with Section PC 608.13.2 of the New York city plumbing code and backflow preventers with intermediate atmospheric vents complying with Section PC 608.13.3 of the New York city plumbing code shall be located at or above the design flood elevation specified in ASCE 24, Table 7-1;

§6. Section BC G304.1.2 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding a new item 2.3.1 to read as follows:

2.3.1 Additional requirements. The structure shall comply with Items 4.1 through 4.4 of Section G304.1.1 and the following additional requirements:

2.3.2 Generators and emergency power systems in hospitals. In I-2 occupancies that are hospitals, generators and fuel pumps serving emergency power systems shall be accessible for maintenance and repair during moderate flood conditions;

§7. Section BC G304.2 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding a new item 5.1 to read as follows:

5.1 Additional requirements. The structure shall comply with Item 2.3.1 of G304.1.2;

§8. Section BC G304 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding a new subsection BC G304.3 to read as follows:

G304.3 Construction standards for areas of moderate flood hazard. In areas of moderate flood hazard, the following standards shall apply to new construction and substantial improvements.

G304.3.1 Hospitals. I-2 occupancies that are hospitals shall be considered to be in A-Zones and shall comply with Section G304.1.2 and the applicable provisions of ASCE 24.

G304.3.2 Fuel-oil piping systems. For fuel-oil piping systems, as defined by Section MC 202 of the New York city mechanical code, fill piping shall terminate three feet (914 mm) above the moderate flood elevation;

§9. Section BC G501.1 of the New York city building code, as amended by local law number 8 for the year 2008, is amended by adding a new subsection 7.2.4 to read as follows:

Section 7.2.4. Section 7.2.4 (Disconnect Switches and Circuit Breakers) is amended to read as follows:

7.2.4 Disconnect Switches and Circuit Breakers. The main disconnect switch, all service disconnecting means, and all circuit breakers and fuse boxes shall be located above and be accessible from the elevation specified in Table 7-1. Switches, all service disconnecting means, and circuit breakers and fuse boxes shall be located no more than 5 ft above the floor, or a platform shall be installed to provide access.

§10. Section BC G307 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding a new section BC G307.4 to read as follows:

G307.4 Elevation of certain tanks and containers serving critical facilities. The following tanks and containers shall be located at or above the greater of (i) the design flood elevation specified in ASCE 24, Table 7-1, or (ii) the moderate flood elevation, when serving structures in structural occupancy category IV, as designated in ASCE 24, Table 1-1. Such tanks and containers must be designed to maintain service to such structure during flood conditions and shall comply with section 9.6 of ASCE 24:

1. Medical and compressed gas storage tanks, oxygen tanks, and other cryogenic system storage tanks;

2. Hazardous material storage tanks;

3. Stationary compressed gas containers;

4. Stationary cryogenic containers; and

5. Stationary flammable gas storage containers.

§11. The definition of “Design Flood Elevation” as set forth in sections 1.2 of section BC G501.1 of the New York city building code, as amended by local law number 8 for the year 2008, is amended to read as follows:

Design Flood Elevation-[The applicable elevation specified in Table 2-1, 4-1, 5-1, 6-1, or 7-1, depending on the structural occupancy category designated in Table 1-1.] As defined in Section G201 of the New York City Building Code, Appendix G.

§12. Section BC 903.3 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding a new subsection BC 903.3.8 to read as follows:

903.3.8 Location of sprinkler booster pumps. Sprinkler booster pumps shall be located in a 2-hour fire-rated enclosure. Such enclosure shall be accessible from a 2-hour fire-rated passageway or stairway.

§13. Section BC 905.2 of the New York city building code, as added by local law number 33 for the year 2007, is amended by adding a new subsection BC 905.2.1 to read as follows:

905.2.1 Location of fire pumps. Fire pumps shall be located in a 2-hour fire-rated enclosure. Such enclosure shall be accessible from a 2-hour fire-rated passageway or stairway.

§14. Section MC 301.13 of the New York city mechanical code, as added by local law number 33 for the year 2007, is amended to read as follows:

301.13 Flood hazard. For structures located in areas of special flood hazard or areas of moderate flood hazard, mechanical systems, equipment and appliances shall comply with Appendix G of the New York City Building Code.

§15. Section FC 903.2 of the New York city fire code, as added by local law number 26 for the year 2008, is amended by adding a new subsection FC 903.2.14 to read as follows:

903.2.14 Flood Hazard. For structures located in areas of special flood hazard, as defined by Section BC G201.2 of the New York city building code, electrically activated sprinkler systems shall be located at or above the design flood elevation specified in Section 7.1 (Table 7-1) of Section BC G501.1 of the New York city building code.

§16. Section FC 904.2 of the New York city fire code, as added by local law number 26 for the year 2008, is amended by adding a new subsection FC 904.2.1 to read as follows:

904.2.1 Flood Hazard. For structures located in areas of special flood hazard, as defined by Section BC G201.2 of the New York city building code, electrically activated fire extinguishing systems shall be located at or above the design flood elevation specified in Section 7.1 (Table 7-1) of Section BC G501.1 of the New York city building code.

§17. Section FC 2703.2.4 of the New York city fire code, as added by local law number 26 for the year 2008, is amended to read as follows:

2703.2.4 Installation of tanks. Installation of tanks shall be in accordance with Sections 2703.2.4.1 through [2703.2.4.2.1] 2703.2.4.3 and with the regulations of the New York State Department of Environmental Conservation as set forth in 6 NYCRR Sections 599.6, 614.7 and 614.13.

§18. Section FC 2703.2.4 of the New York city fire code, as added by local law number 26 for the year 2008, is amended by adding a new subsection FC 2703.2.4.3 to read as follows:

2703.2.4.3 Flood Hazard. Notwithstanding any other provision in this section, for structures located in areas of special flood hazard, as defined by Section BC G201.2 of the New York city building code, hazardous material storage tanks shall comply with Section BC G307.4 of the New York city building code.

§19. Section FC 3003.3.3 of the New York city fire code, as added by local law number 26 for the year 2008, is amended by adding a new subsection FC 3003.3.3.1 to read as follows:

3003.3.3.1 Flood Hazard. Notwithstanding any other provision in this section, for structures located in areas of special flood hazard, as defined by Section BC G201.2 of the New York city building code, stationary compressed gas containers shall comply with Section BC G307.4 of the New York city building code.

§20. Section FC 3203.1.2 of the New York city fire code is REPEALED and replaced with a new section FC 3203.1.2 to read as follows:

3203.1.2 Flood Hazard. Notwithstanding any other provision in this section, for structures located in areas of special flood hazard, as defined by Section BC G201.2 of the New York city building code, stationary cryogenic containers shall comply with Section BC G307.4 of the New York city building code.

§21. Section FC 3503.1.2 of the New York city fire code, as added by local law number 26 for the year 2008, is amended by adding a new subsection FC 3503.1.2.1 to read as follows:

3503.1.2.1 Areas of Special Flood Hazard. Notwithstanding any other provision in this section, in areas of special flood hazard, as defined by Section BC G201.2 of the New York city building code, stationary flammable gas containers shall comply with Section BC G307.4 of the New York city building code.

§22. This local law shall take effect immediately.

EAA

6/20/2013 4:35PM