LOCAL LAWS

OF

THE CITY OF NEW YORK

FOR THE YEAR 2002

No. 26

Introduced by Council Members Provenzano, Addabbo Jr., Baez, Clarke, Comrie, Davis, Gerson, Lopez, Nelson, Recchia Jr., Rivera, Weprin, Vallone Jr., Lanza and Golden (by request of the Mayor); also Council Member Seabrook

## A LOCAL LAW

To amend the administrative code of the city of New York, in relation to requiring the installation of fire sprinklers in connection with the below-grade storage of flammable and combustible mixtures in mercantile occupancies.

Be it enacted by the Council as follows:

Section 1.  Section 27-929 of the administrative code of the city of New York, as amended by local law number 16 for the year 1987, is amended by adding a new subdivision c to read as follows:

(c)  Notwithstanding any other provision of this subchapter, the requirement to install a system of automatic sprinklers shall apply retroactively to any space in a basement, cellar or other location below grade subject to the provisions of subdivision aa of section 27-954 of this code.  Installation of such system of automatic sprinklers shall be completed on or before April thirtieth, two thousand four.

§2.  Section 27-954 of the administrative code of the city of New York is amended by adding a new subdivision aa to read as follows:

(aa) Regardless of occupancy group classification, in each basement, cellar or other location below grade, regardless of the floor area of such space, in any mercantile establishment in which the fire commissioner permits the storage of flammable or combustible mixtures pursuant to sections 27-4066, 27-4070 or 27-4094 of this code, except that, where such flammable or combustible mixtures are stored in such basement, cellar or other location below grade, in a room or other area that is segregated, vertically and horizontally, from surrounding spaces by a fire separation of not less than a two-hour fire-resistance rating, such system of automatic sprinklers shall be required only within such room or other area.  Such system of automatic sprinklers shall conform to the requirements for automatic sprinklers for spaces classified in storage occupancy group B-1 pursuant to subdivision d of this section.

§3.  Table 17-2 of article 4 of subchapter 17 of chapter 1 of title 27 of the administrative code of the city of New York, as amended by local law number 10 for the year 1999, is amended by amending line four to read as follows:

TABLE 17-2  SUMMARY OF SPRINKLER REQUIREMENTS

| Where Required Type of System | Automatic Sources Required | Partial System Permitted | Connection to Domestic Permitted | Alternate Permitted (§27-955) | Siamese Required (§27-959) | Centrala Station Required (§27-955) (§27-967) | Waterb Flow Alarm Required (§27-957) | Automatic Dry Sprinkler Permitted (§5212 of RS17) | Dry Nonautomatic Sprinkler Permittedc |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Storage Occupancy Spaces – Group B1 (§27-954 (d)) and Permitted Below Grade Flammable/ Combustible Storage Spaces in Mercantile Establishments (§27-954(aa)) | 1 | # Yes | Yes, [§27-961(c)] §27-962(c) | No | §27-959(a)(3), If over 36 heads in a fire section | Nonea | Yesb, If over 36 heads in a fire section | Yes | No |

§4. Subdivision c of section 27-962 of the administrative code of the city of New York is amended to read as follows:

(c) The domestic water supply may be used to supply any sprinklers required under section 27-954 of this article when installed in buildings classified in occupancy groups E, G, H and J, or to supply any sprinklers required under subdivision (aa) of said section, regardless of occupancy group classification, provided that all the requirements stated in subdivision e of section 27-962 of this article are met.

§5. Section 27-4066 of the administrative code of the city of New York is amended by adding a new subdivision e to read as follows:

e. A system of automatic sprinklers shall be provided in each basement, cellar or other location below grade, regardless of the floor area of such space, in any mercantile establishment in which the commissioner permits the storage of flammable mixtures, except that, where flammable mixtures are stored in such basement, cellar or other location below grade, in a room or other area that is segregated, vertically and horizontally, from surrounding spaces by a fire separation of not less than a two-hour fire-resistance rating, such system of automatic sprinklers shall be required only within such room or other area.  Such system of automatic sprinklers shall conform to the requirements for automatic sprinklers for spaces classified in storage occupancy group B-1 pursuant to subdivision d of section 27-954 of the building code.

§6. Section 27-4070 of the administrative code of the city of New York is amended by adding a new subdivision d to read as follows:

d. A system of automatic sprinklers shall be provided in each basement, cellar or other location below grade, regardless of the floor area of such space, in any mercantile establishment in which the commissioner permits the storage of combustible mixtures, except that, where combustible mixtures are stored in such basement, cellar or other location below grade, in a room or other area that is segregated, vertically and horizontally, from surrounding spaces by a fire separation of not less than a two-hour fire-resistance rating, such system of automatic sprinklers shall be required only within such room or other area.  Such system of automatic sprinklers shall conform to the requirements for automatic sprinklers for spaces classified in storage occupancy group B-1 pursuant to subdivision d of section 27-954 of the building code.

§7.  The first sentence of Section 27-4094 of the administrative code of the city of New York is amended to read as follows:

§27-4094.  Restrictions. a. No permit for the manufacture, mixing or compounding of paints, varnishes or lacquers shall be issued for any premises:

§8.  Section 27-4094 of the administrative code of the city of New York is amended by adding a new subdivision b to read as follows:

b. A system of automatic sprinklers shall be provided in each basement, cellar or other location below grade, regardless of the floor area of such space, in any mercantile establishment in which the commissioner permits the storage of flammable or combustible paints, varnishes, lacquers or other substances, mixtures or compounds commonly used for painting, varnishing, staining or similar purposes, except that, where such flammable or combustible substances, mixtures or compounds are stored in such basement, cellar or other location below grade, in a room or other area that is segregated, vertically and horizontally, from surrounding spaces by a fire separation of not less than a two-hour fire-resistance rating, such system of automatic sprinklers shall be required only within such room or other area.  Such system of automatic sprinklers shall conform to the requirements for automatic sprinklers for spaces classified in storage occupancy group B-1 pursuant to subdivision d of section 27-954 of the building code.

§9. This local law shall take effect immediately, provided however, that any mercantile establishment existing on the date of enactment that lacks a system of automatic sprinklers required by this local law shall not be deemed to be in violation of the requirements of this local law if it is brought into compliance with such requirements on or before April thirtieth, two thousand four.

THE CITY OF NEW YORK, OFFICE OF THE CITY CLERK, s.s.:

I hereby certify that the foregoing is a true copy of a local law of the city of New York, passed by the Council on August 15, 2002, and approved by the Mayor on September 4, 2002.

VICTOR L. ROBLES, City Clerk Of The Council.

CERTIFICATION PURSUANT TO MUNICIPAL HOME RULE LAW §27

Pursuant to the provisions of Municipal Home Rule Law §27, I hereby certify that the enclosed Local Law (Local Law 26 of 2002, Council Int. No. 203-A) contains the correct text and:

Received the following vote at the meeting of the New York City Council on August 15, 2002:   45 for, 0 against, 0 not voting.

Was signed by the Mayor on September 4, 2002.

Was returned to the City Clerk on September 5, 2002.

JEFFREY D. FRIEDLANDER, Acting Corporation Counsel