Int. No. 262

By Council Members Cabrera, Brewer, Foster, James, Lander, Palma, Reyna, Sanders Jr., Mark-Viverito, Van Bramer, Recchia, Weprin, Gennaro, Jackson and Garodnick

..Title

A Local Law to amend the administrative code of the city of New York, in relation to reducing unnecessary artificial lighting in lobbies and hallways.

..Body

Be it enacted by the Council as follows:

Section 1.  Statement of findings and purpose.  The Council finds that current egress illumination requirements for lobbies and hallways under the New York City Building Code result in the artificial lighting of egress spaces which are either sufficiently lit by natural lighting or which are unoccupied.  The Council therefore finds that energy could be saved by reducing such excessive lighting requirements for such spaces.

§2.  Sections 1006.1 and 1006.2 of the New York City building code are amended to read as follows:

1006.1 Illumination Required. Exits, exit discharges, and public corridors shall be illuminated at all times by either natural light or electrical lighting fixtures. Exit access components shall be illuminated by either natural light or electrical lighting fixtures at all times [during occupancy] that the space served by the exit access component is occupied.

Exceptions:

1.  Occupancies in Group U.

2.  Aisle accessways in Group A.

3. Dwelling units and sleeping units in Groups I-1, R-1, R-2 and R-3.

4.  Sleeping units of Group I occupancies.

1006.2 Illumination level. The means of egress illumination level shall not be less than [2 foot-candles (22 lux) at the floor level in exits, at exit discharges, and in public corridors, and shall not be less than 1 foot-candle (11 lux) at the floor level in exit access components other than public corridors] 1 foot-candle (11 lux) at the walking surface level.

Exceptions:

1.	For auditoriums, theaters, concert or opera halls and similar assembly occupancies, the illumination at the floor level is permitted to be reduced during performances to not less than 0.5 foot-candle (5.38 lux) for aisles and cross aisles, and 0.2 foot-candle (2.15 lux) for other portions of the space, provided that the required illumination is automatically restored upon activation of a premise’s fire alarm system where such system is provided. Step lights shall be provided in accordance with Section 1024.11.4.

2. 	Safe areas in assembly occupancies shall be illuminated in accordance with Section 1024.17.3.2.

3. 	Open exterior spaces used to receive occupants as Class 1 or 2 exits in assembly occupancies shall be illuminated in accordance with Section 1024.17.4.

4.	In exits in existing buildings that contain photoluminescent exit path markings tested in laboratory conditions with 2 foot-candles (22 lux) of activating illumination, the illumination level shall not be less than 2 foot-candles (22 lux).

§3.  Section 1006 of the New York city building code is amended by adding a new section 1006.2.1 to read as follows:

1006.2.1 Sensors and Controls. Automatic, occupant sensor or photo-sensor lighting controls shall be permitted within means of egress, provided that the illumination level is not reduced to a level below the minimum requirements of section 1006.2.

§4.  This local law shall take effect on January 1, 2011, except that the commissioner of buildings shall take such actions as are necessary for its implementation, including the promulgation of rules, prior to such effective date.

.

LS 1001

06-04-10, 11 am

db