Int. No. 1094

By Council Members Mendez, Brewer, Chin, James, Lander, Richards and Rose

..Title

A Local Law to amend the New York city plumbing code and the administrative code of the city of New York, in relation to requiring residential buildings to provide drinking water to a common area supplied directly through pressure in the public water main.

..Body

Be it enacted by the Council as follows:

Section 1.The New York city plumbing code is amended by adding a new section PC 614 to read as follows:

SECTION PC 614

EMERGENCY DRINKING WATER ACCESS

614.1 Buildings required to provide alternative potable water access. Buildings with residential occupancies that have a source of water supply other than the public water main, or that have a water pressure booster pump installed in accordance with Section 606.5, shall provide an emergency source of water supply for human ingestion in accordance with Sections 614.1.1 through 614.1.6.

614.1.1 Emergency source of water fixture. An emergency source of water fixture shall  consist of a faucet for supplying drinking water for human ingestion conforming to Section 424 supplied only by street pressure from the public water main, and either:

1. a sink conforming to Section 418; or

2. a floor drain conforming to Section 412.

614.1.2 Number of fixtures required. One emergency source of water fixture for 75 residents as determined by the occupant load of in the building.

614.1.3 Accessibility. Emergency source of water fixtures shall be located indoors in an area that is accessible to all tenants of the building.

614.1.4 Signage. Required emergency source of water fixtures shall be designated by a legible sign stating: “EMERGENCY DRINKING WATER.” Signs shall be readily visible and located near the emergency source of water fixture, and on the door to any room or closet in which the fixture is located.

614.1.5 Location. For any building that is located in a special flood hazard area and is in existence as of January 1, 2014, all emergency source of water fixtures shall be located on a story that is entirely above the design flood elevation specified in ASCE 24, Table 7-1, as modified by Appendix G of the New York City Building Code. Emergency source of water fixtures shall not be located in a bathroom or toilet room.

614.1.6 Applicability. On and after January 1, 2019, the requirements of this Section shall be required for all buildings with residential occupancies that have a source of water supply other than the public water main, or that have a water pressure booster pump installed in accordance with Section 606.5.

§ 2. Section 28-101.4.3 of the administrative code of the city of New York is amended by adding new item 14 to read as follows:

14. Emergency source of water supply for human ingestion shall be provided in accordance with section 614 of the New York city plumbing code.

§ 3. Chapter 3 of title 28 of the administrative code of the city of New York is amended by adding a new article 314 to read as follows:

ARTICLE 314

EMERGENCY DRINKING WATER

§28-314.1 Retroactive requirement for residential occupancies. On and after January 1, 2019, the provisions of section 614 of the New York city plumbing code requiring emergency source of water supply for human ingestion shall apply retroactively to all buildings in existence on January 1, 2014.

§ 4. This local law shall take effect on January 1, 2014.

JCH

6/21/2013 12:58 PM