Int. No. 986

By Council Member Baez, the Speaker (Council Member Quinn) and Council Members Vallone Jr., Avella, Fidler, Gentile, Gonzalez, James, Koppell, Liu, Nelson, Sanders Jr., Weprin, Gerson and Lappin (in conjunction with the Mayor).

..Title

A Local Law to amend the administrative code of the city of New York and the New York city building code, in relation to hydrostatic pressure testing of standpipes and sprinklers.

..Body

Be it enacted by the Council as follows:

Section 1.  Subsection 1704.21 of section BC 1704 of chapter 17 of the New York city building code of chapter 7 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, is amended and a new subsection 1704.21.1 is added to read as follows:

1704.21 Sprinkler system special inspection. New and altered sprinkler [system] systems shall be inspected in accordance with [Section] Sections 903 and 1704.21.1. The permit holder responsible for the sprinkler work shall perform all required acceptance tests, complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests, and shall verify that all installations of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that any painting of the sprinkler system required by Section 903.6 has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the department.

Exception: [Special inspection of] The special inspector need not witness the hydrostatic test [shall not be required] when such test is witnessed by the department.

1704.21.1  Hydrostatic pressure testing.  All new or altered sprinkler systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5, and NFPA 13 § 10.10.2.2, as modified in Appendix Q.

§2.  Subsection  1704.22 of Section BC 1704 of chapter 17 of the New York city building code of chapter 7 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, is amended and a new subsection 1704.22.1 is added to read as follows:

1704.22 Standpipe system special inspection. New and altered standpipe systems shall be inspected in accordance with [Section] Sections 905 and 1704.22.1. The permit holder responsible for the standpipe work shall perform all required acceptance tests, complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests, verify that installation of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that any painting of the standpipe system required by Section 905.11 has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the department.

Exception:  [Special inspection of] The special inspector need not witness the hydrostatic test [shall not be required]when such test is witnessed by the department.

1704.22.1  Hydrostatic pressure testing.  All new or altered standpipe systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5, Sections 1704.22.1.1 through 1704.22.1.5 and NFPA 14 §11.4.

1704.22.1.1  New buildings. An initial test shall be performed when the building reaches a height of 75 feet (22 860 mm) and additional tests shall be performed at every 75 feet (22 860 mm) thereafter.  The permit holder shall perform a final test of the completed system in accordance with the requirements of Section 901.5.

1704.22.1.2  Enlargements or additions to existing system.  Where there is an enlargement that triggers a new standpipe system or there is an addition to an existing standpipe system, hydrostatic tests shall be performed every 75 feet (22 860 mm).  The permit holder shall perform a final test of the completed system in accordance with the requirements of Section 901.5.

1704.22.1.3  Removal of stories.  Where stories are removed from a building served by an existing standpipe system, hydrostatic testing shall be performed prior to the commencement of work if the building is in violation of Sections 905.12, 905.12.1 and 912.6 of the New York City Fire Code.

1704.22.1.4  Alterations.  For alterations not covered under sections 1704.22.1.2 or 1704.22.1.3, above, the permit holder shall perform a final test of the completed system in accordance with the requirements of Section 901.5.

1704.22.1.5  Readiness. No standpipe system shall be considered in readiness until there has been a successful hydrostatic test.

§3.  This local law shall take effect six months after enactment except that the commissioner of buildings may promulgate rules or take other administrative actions for the implementation of this local law prior to such effective date.

RCC

BKH

5/14/09

1:30 p.m.

LS # 6583